4-inch IR Speed Dome Installation Manual

Version 1.0.1

Table of Contents

1	SPEED DOME INSTALLATION	1

1.1	Installation Environments	1

1.2	Check installation space and installation location intension	1

1.3	About cable	1

1.4	Select required power supply cable according to transmission distance	2

1.5	Please keep all package material well for future use	2

2	SETUP BEFORE INSTALLATION	3

2.1	Check Accessories	3

2.2	Open Device	3

2.3	Dial Switch Setup	3

2.3.1	Dial Location and Function	3

2.3.2	Dial Setting	5

2.3.3	Address Setting	5

2.3.4	Baud Rate, Parity and HD/SD Video Mode Setting	5

2.3.5	Terminal Matching Resistance Setup	6

2.4	RESET and SD Card Installation (Network Speed Dome)	7

2.5	Cable Connection	7

3	INSTALLATION	8

3.1	Component Installation	8

3.2	Wall Mount Installation Steps	9

3.2.1	Installation Environments	9

3.2.2	Installation Steps	9

4	APPENDIX Ⅰ LIGHTENING PROTECTION AND SURGE PROTECTION	11

5	APPENDIX Ⅱ ABOUT RS485 BUS	12

5.1	RS485 Bus Main Feature	12

5.2	RS485 Bus Transmission Distance	12

5.3	The Problem in Practical Use	12

5.4	RS485 Bus FAQ	13

6	APPENDIX Ⅲ THE AC 24V WIRE GAUGE AND  TRANSMISSION DISTANCE RELATIONSHIP SHEET	14

7	APPENDIX Ⅳ DC 12V WIRE GAUGE AND TRANSMISSION DISTANCE RELATIONSHIP SHEET	15

8	APPENDIX V WIRE GAUGE REFERENCE SHEET	16

Welcome

Thank you for purchasing our speed dome!

Please read the following safeguards and warnings carefully before you install or use the product!

Important Safeguards and Warnings

Safety Measures

1. Qualified Engineer Needed

- The installation engineer or maintenance engineer shall have corresponding CCTV system installation certificate or maintenance qualification certificate.

- The installation engineer or maintenance engineer shall have qualification certificate for work at height.

- The installation engineer or maintenance engineer shall have the basic knowledge and operation technique for low-voltage cable layout and low-voltage electronic cable connection.

- Please read the installation manual carefully and keep it well for future reference,

- We are not liable for any problems caused by unauthorized modifications or attempted repair.

2. Lifting Appliance Requirement

- Please select the proper speed dome installation mode and use the lifting appliances at the safety environment.

- The lifting appliances shall have the enough capacity to reach the installation height.

- The lifting appliances shall have safe performance.

The precaution measures include two types: Warning and Note.

- Warning: It is to alert you there is an optional risk of death or series injury!

- Note: It is to alert you there is an optional risk of damage or property loss!

Warning

- All installation and operation here should conform to your local electrical safety codes.

- The power shall conform to the requirement in the SELV (Safety Extra Low Voltage) and the rated voltage conformed to Limited Power Source according to the IEC60950-1. (Power supply requirement is subject to the device label).  We assume no liability or responsibility for all the fires or electrical shock caused by improper handling or installation.

- Be sure to use all the accessories (such as power adapter) recommended by manufacturer.

- Do not connect several speed domes to one power adapter. It may result in overheat or fire if it exceeds the rated load.

- Before you connect the cable, install or uninstall, or begin the daily maintenance work, please turn off the power and unplug the power cable.

- Please make sure the produce is secure firmly on the wall or the ceiling.

- Please turn off the power and unplug the power cable, If there is any smoke, disgusting smell, or noise. Please contact your local retailer or customer service centre for help.

- All the examination and repair work should be done by the qualified service engineers.  We are not liable for any problems caused by unauthorized modifications or attempted repair.

- Please fix the intelligent speed dome firmly if it is installed on the wall or ceiling.

Note

1. Safety Transportation

- Heavy stress, violent vibration or water splash are not allowed during transportation, storage and installation.

- This series product must use split type package during the transportation.

- We are not liable for any damage or problem resulting from the integrated package during the transportation.

2. When device is malfunction

Shut down the device and disconnect the power cable immediately if there is smoke, abnormal smell or abnormal function. Please contact your local retailer ASAP.

3. Do not try to dismantle or modify the device

- There is risk of personal injury or device damage resulting from opening the shell.

- Please contact your local retailer if there is internal setup or maintenance requirement.

- We are not liable for any problems caused by unauthorized modifications or attempted repair.

4. Do not allow other object falling into the device

- Please make sure there is no metal or inflammable, explosive substance in the speed dome.

- The above mentioned objects in the device may result in fire, short-circuit or damage.

- Please shut down the device and disconnect the power cable if there is water or liquid falling into the camera. Please contact your local retailer ASAP.

- Please pay attention to the camera. Avoid the sea water or rain to erode the camera.

5. Handle carefully

Do not allow this series product fall down to the ground.

Avoid heavy vibration.

6. Installation Environment Requirement

- This series speed dome should be installed in a cool, dry place away from direct sunlight, inflammable, explosive substances and etc.

- This series product shall be away from the strong electromagnetism radiant, please keep it away from wireless power, TV transmitter, transformer and etc.

7. Daily Maintenance

- Please use the soft cloth to clean dust on the shell, or you can use soft cloth with cleaning liquid to clean the shell and then use soft cloth to make it dry.

- Do not use gasoline, dope thinner or other chemical material to clean the shell. It may result in shell transfiguration or paint flake.

- Do not allow the plastic or rubber material to touch the shell for a long time. It may result in paint flake.

# SPEED DOME INSTALLATION

## Installation Environments

Basic Requirement

- All installation and operation here should conform to your local electrical safety codes.

- Before installation, please open the package and check all the components are included. Please make sure the speed dome installation environment and installation mode can meet your requirement. If there is special requirement, please contact your local retailer for more information.

- We assume no liability or responsibility for all the fires or electrical shock caused by improper handling or installation.

## Check installation space and installation location intension

Please make sure the installation environment has enough space to install the speed dome and its corresponding bracket.

Please make sure the ceiling, wall and the bracket can support the speed dome and its corresponding installation component. It shall sustain the 8X weight of the speed dome.

## About cable

Please select the cable according to your transmission distance.

The minimum video coaxial-cable requirement is:

- 75 ohm.

- Full cable with copper conductor

- 95% knitted copper shield

- RS485 communication cable, refer to appendix 2

| International Model | Max Transmission Distance (Ft\M) |
| --- | --- |
| RG59/U | 750Ft (229M) |
| RG6/U | 1,000Ft (305M) |
| RG11/U | 1,500Ft (457M) |

Note:

The above can be applied to analog speed dome and network speed dome

| International Mode | Max Transmission Distance(Ft\M) |
| --- | --- |
| SYV-75-3 | 720P（25fps\30fps)：500M/1640Ft |
|  | 720P（50fps\60fps)：300M/984Ft |
|  | 1080P（25fps\30fps):300M/984Ft |

Note:

The above can be applied to HDCVI speed dome

## Select required power supply cable according to transmission distance

- For AC 24V series product, please refer to Appendix 3.

- For DC 12V series product, please refer to Appendix 4.

## Please keep all package material well for future use

Please keep speed dome package material well in case you need to send it back to your local retailer or manufacturer for maintenance work.

Note:

Non-original package material may result in device damage during the transportation.

# SETUP BEFORE INSTALLATION

## Check Accessories

Before the installation, please check the accessories one by one according to the packing list. Please make sure all the components listed are included.

## Open Device

Remove the package and then take out the device. See Figure 2-1.

Figure 2-1

## Dial Switch Setup

### Dial Location and Function

The corresponding functions of dial switch for analog speed dome and HDCVI speed dome are different, which will be respectively introduced below.

#### Analog Speed Dome

Open the rear cover and you can see there is a dial switch on the PTZ mainboard which you can use to set the speed dome address, baud rate and parity etc. See Figure 2-2.

Figure 2-2

#### HDCVI Speed Dome

Open the rear cover and you can see there is a dial switch on the PTZ mainboard which you can use to set the speed dome address, baud rate and HD/SD video format etc. Please refer to Figure 2-3.

Figure 2-3

### Dial Setting

Before you control the speed dome, please set the speed dome address number, baud rate, and parity or HD/SD video mode. The speed dome will respond to its control command after completing all these settings.

Note:

Open speed dome rear cover, you can see the dial switch buttons on the PTZ mainboard. You can follow the steps listed below to set the speed dome address number, baud rate, and parity or HD/SD video mode. Please be noted that you need to restart the device to activate the new settings.

The dial switches on the PTZ are used to set speed dome address, baud rate, and parity or HD/SD video mode parameters. When you switch ON as 1, then 1 is the lowest bit and 8 is the highest bit in address setting dial switch; for baud rate and parity or HD/SD video mode setting, 9 is the lowest bit and 12 is the highest bit.

Note:

Please be noted that the speed dome can self-adapt to the industrial standard protocol, PELCO-D and PELCO-P, the control protocol doesn’t need to be set via dial setting.

### Address Setting

The speed dome uses dial switch to set address number, the encoding mode adopts binary system. 1 to 8 is valid bit, and the highest address bit is 255. You can refer to sheet 2-1 for more information about address number setting.

| Address | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF |
| 1 | ON | OFF | OFF | OFF | OFF | OFF | OFF | OFF |
| 2 | OFF | ON | OFF | OFF | OFF | OFF | OFF | OFF |
| 3 | ON | ON | OFF | OFF | OFF | OFF | OFF | OFF |
| 4 | OFF | OFF | ON | OFF | OFF | OFF | OFF | OFF |
| 5 | ON | OFF | ON | OFF | OFF | OFF | OFF | OFF |
| 6 | OFF | ON | ON | OFF | OFF | OFF | OFF | OFF |
| 7 | ON | ON | ON | OFF | OFF | OFF | OFF | OFF |
| 8 | OFF | OFF | OFF | ON | OFF | OFF | OFF | OFF |
| …… | ………………………………………………………………… |
| 254 | OFF | ON | ON | ON | ON | ON | ON | ON |
| 255 | ON | ON | ON | ON | ON | ON | ON | ON |

Sheet 2-1

### Baud Rate, Parity and HD/SD Video Mode Setting

#### Analog Speed Dome

Bit 9 and 10 are used to set baud rate in the dial bit from 9 to 12, bit 11 and 12 are used to set parity. Please refer to sheet 2-2 and 2-3 for detailed information.

| 9 | 10 | Baud Rate |
| --- | --- | --- |
| OFF | OFF | 9600bps |
| ON | OFF | 4800bps |
| OFF | ON | 2400bps |
| ON | ON | 1200bps |

Sheet 2-2

| 11 | 12 | Parity |
| --- | --- | --- |
| OFF | OFF | NONE |
| ON | OFF | EVEN |
| OFF | ON | ODD |
| ON | ON | NONE |

Sheet 2-3

#### HDCVI Speed Dome

Bit 9 and 10 are used to set baud rate in the dial bit from 9 to 12, bit 11 and 12 are used to set HD/SD video mode. Please refer to sheet 2-4 and 2-5 for detailed information.

| 9 | 10 | Baud Rate |
| --- | --- | --- |
| OFF | OFF | 9600bps |
| ON | OFF | 4800bps |
| OFF | ON | 2400bps |
| ON | ON | 1200bps |

Sheet 2-4

| 11 | 12 | Parity |
| --- | --- | --- |
| OFF | OFF | HD |
| ON | OFF | SD |
| OFF | ON | Self-adapt |
| ON | ON | HD |

Sheet 2-5

### Terminal Matching Resistance Setup

The connection mode of device terminal 120Ω resistance, the terminal resistance 120Ω already exists on the power board, there are two connection modes, see Figure 2-4.

Figure 2-3

The factory default setup is shown as in Figure 2-5. Right now, the jumper (Connection board) is on the pin 2 and pin 3. The 120Ω resistance does not connect to the device.

Figure 2-5

If you want to connect the 120Ω resistance, please remove the jumper from the pin 2 and pin 3 and connect to pin 1 and pin 2. Now the 120Ω is connected to the circuit. See Figure 2-6.

Figure 2-6

## RESET and SD Card Installation (Network Speed Dome)

Open the rear cover and you can see there is a reset button and a SD card slot on the PTZ mainboard (see Figure 2-7). The reset button is used to reset network system and SD card is used to store data.

Figure 2-7

## Cable Connection

Please connect the power cable, video output cable, audio cable, RS485 control cable, alarm input/output pin, network cable, and high-frequency cable well according to your actual requirements. Please use insulation tape to seal the cable connection ports to do proper waterproof work.

Note

The video port is covered the heat shrink tube of high shrinking ratio. After the video connection, please heat the tube to make sure the video port is damp proof and waterproof.

# INSTALLATION

The IR intelligent speed dome mainly adopts wall mount mode.

## Component Installation

The wall mount bracket is shown in Figure 3-1 and Figure 3-2.

Figure 3-1

Figure 3-2

## Wall Mount Installation Steps

### Installation Environments

The wall mount speed dome can be installed in the hard construction wall in the indoor or outdoor environments.  Before the installation, please make sure:

- The wall is thick enough to install the expansion bolt.

- The ceiling can at least sustain the 8x weight of the speed dome, bracket and the accessories.

### Installation Steps

Step 1

Draw the punch positions on the wall according to the installation holes on the bottom of the wall mount bracket (align the bracket cable outlet hole with the round hole on the wall), and dig holes on the wall, then insert the expansion bolts into the holes which were just dug (expansion bolts are prepared by users themselves).

Step 2

As it is shown in Figure 3-3, lock the safety buckle well; insert the combination cable of the speed dome from the adapter and pull it out from the other end of the wall mount bracket, then aim the enclosure top connecting flange at the inner holes of the adapter, push the speed dome to the bottom and tighten the three screws completely just in case the speed dome falls if it is not installed properly.

Figure 3-3

Step 3

Insert the combination cable into the wall holes after it is connected respectively, and then use four hex nuts and flat gasket to fix the wall mount bracket on the wall where expansion bolts are already inserted, see Figure 3-4.

Figure 3-4

Step 4

Now the installation of the speed dome is completed, see Figure 3-5.

Figure 3-5

# APPENDIX Ⅰ LIGHTENING PROTECTION AND SURGE PROTECTION

This series speed dome adopts TVS lighting protection technology. It can effectively prevent damages from various pulse signals below 6000W, such as sudden lighting and surge. While maintaining your local electrical safety code, you still need to take necessary precaution measures when installing the speed dome in the outdoor environment.

- The distance between the signal transmission cable and high-voltage device (or high-voltage cable) shall be at least 50 meters.

- Outdoor cable layout shall go under the penthouse if possible.

- For vast land, please use sealing steel tube under the land to implement cable layout and connects one point to the earth. Open floor cable layout is forbidden.

- In area of strong thunderstorm hit or near high sensitive voltage (such as near high-voltage transformer substation), you need to install additional high-power thunder protection device or lightning rod.

- The thunder protection and earth of the outdoor device and cable shall be considered in the building whole thunder protection and conform to your local national or industry standard.

- System shall adopt equal-potential wiring. The earth device shall meet anti-jamming and at the same time conforms to your local electrical safety code. The earth device shall not short circuit to N (neutral) line of high voltage power grid or mixed with other wires. When connect the system to the earth alone, the earth resistance shall not be more than 4Ω and earth cable cross-sectional area shall be below 25 mm². See Figure 4-1.

Figure 4-1

# APPENDIX Ⅱ ABOUT RS485 BUS

## RS485 Bus Main Feature

RS485 is semi duplex communication cable of impedance 120Ω. Its max load amount is 32 effective loads (including main control device and devices to be charged).

## RS485 Bus Transmission Distance

When we take 0.56mm (24AWG) twisted-pair as communication cable, the max transmission distance (theoretically) are listed below (according to different baud rates).

| Baud Rate | Max Distance |
| --- | --- |
| 2400 BPS | 1800M |
| 4800 BPS | 1200M |
| 9600 BPS | 800M |

In the following situations, the max transmission distance shall become shorter accordingly:

- The communication cable is a little bit thin;

- The surrounding environment has strong electromagnetic interference;

- There are too much devices connected to the RS485 bus;

And vice versa, the max transmission distance shall become longer.

## The Problem in Practical Use

In practical usage, we usually adopt star type connection. The terminal resistance shall connect to the furthest two devices (Such as device 1# and device 15# in Figure 5-1 ). But this connection way does not conform to RS485 Bus standard. When the distances between devices are too long, the signal reflection occurs and anti-jamming decreases, thus the signal reliability becomes very low. You can see speed dome is not under control or speed dome is running automatically and can not stop.

Figure 5-1

In this situation, we recommend RS485 distributor. This device can turn star type connection into the connection that conforms to RS485 bus industry standard, which can avoid the above mentioned problems and enhance communication reliability. See Figure 5-2.

Figure 5-2

## RS485 Bus FAQ

| Phenomenon | Possible Reasons | Solution |
| --- | --- | --- |
| Speed dome can run self-diagnosis but I can not control it. | Host address(baud rate) and speed dome address(baud rate) are not match; Positive and negative end of RS485 Bus are misconnected; Connection cable is loose； RS485 Bus connection are cut off; | Modify host or speed dome setup ； Switch RS485 positive end and negative end； Fix connection cable firmly； Replace RS485 Bus. |
| I can control the speed dome but is not smooth | RS485 Bus connection are not good； One RS485 bus is off； The distance between host and speed dome is too far； Parallel connected too much speed domes. | Connect RS 485 Bus again； Replace RS485 Bus； Add terminal matching resistance； Add RS485 distributor. |

# APPENDIX Ⅲ THE AC 24V WIRE GAUGE AND  TRANSMISSION DISTANCE RELATIONSHIP SHEET

It is the recommended transmission distance when the cable diameter is fixed and the 24V AC power consumption is below 10%. For the AC device, the max permission voltage power consumption is 10%. For example, when a device of rated power 20W installed from the transformer 141 inches (42m), then the min cable diameter is 0.8000mm.

| mm Feet（m） w | 0.8000 | 1.000 | 1.250 | 2.000 |
| --- | --- | --- | --- | --- |
| 5 | 488.52（148.90） | 763.31（232.66） | 1192.67（363.53） | 3053.25（930.63） |
| 10 | 244.26（74.45） | 381.66（116.33） | 596.34（181.76） | 1526.62（465.31） |
| 15 | 162.84（49.63） | 254.44（77.55） | 397.56（121.18） | 1017.75（310.21） |
| 20 | 122.13（37.23） | 190.83（58.16） | 298.17（90.88） | 763.31（232.66） |
| 25 | 97.70（29.78） | 152.66（46.53） | 238.53（72.71） | 610.65（186.13） |
| 30 | 81.42（24.82） | 127.22（38.78） | 198.78（60.59） | 508.87（155.10） |
| 35 | 69.79（21.27） | 109.04（33.24） | 170.38（51.93） | 436.18（132.95） |
| 40 | 61.06（18.61） | 95.41（29.08） | 149.08（45.44） | 381.66（116.33） |
| 45 | 54.28（16.54） | 84.81（25.85） | 132.52（40.39） | 339.25（103.40） |
| 50 | 48.85（14.89） | 76.33（23.27） | 119.27（36.35） | 305.32（93.06） |
| 55 | 44.41（13.54） | 69.39（21.15） | 108.42（33.05） | 277.57（84.60） |
| 60 | 40.71（12.41） | 63.61（19.39） | 99.39（30.29） | 254.44（77.55） |
| 65 | 37.58（11.45） | 58.72（17.90） | 91.74（27.96） | 234.87（71.59） |
| 70 | 34.89（10.64） | 54.52（16.62） | 85.19（25.97） | 218.09（66.47） |
| 75 | 32.57（9.93） | 50.89（15.51） | 79.51（24.24） | 203.55（62.04） |
| 80 | 30.53（9.31） | 47.71（14.54） | 74.54（22.72） | 190.83（58.16） |
| 85 | 28.74（8.76） | 44.90（13.69） | 70.16（21.38） | 179.60（54.74） |
| 90 | 27.14（8.27） | 42.41（12.93） | 66.26（20.20） | 169.62（51.70） |
| 95 | 25.71（7.84） | 40.17（12.25） | 62.77（19.13） | 160.70（48.98） |
| 100 | 24.43（7.45） | 38.17（11.63） | 59.63（18.18） | 152.66（46.53） |

# APPENDIX Ⅳ DC 12V WIRE GAUGE AND TRANSMISSION DISTANCE RELATIONSHIP SHEET

The recommended max transmission distance is under the following environments: The wire diameter is fixed and the DC 12V power voltage loss rate is below 10%. For the device of DC power supplying, the max allowed voltage loss rate is 10%. All the wires listed in the following sheet are copper wire. (Copper wire resistance)

| mm Feet（m） w | 0.8000 | 1.000 | 1.250 | 2.000 |
| --- | --- | --- | --- | --- |
| 5 | 122.13（37.23） | 190.83（58.16） | 298.17（90.88） | 763.31（232.66） |
| 10 | 61.06（18.61） | 95.41（29.08） | 149.08（45.44） | 381.66（116.33） |
| 15 | 40.71（12.41） | 63.61（19.39） | 99.39（30.29） | 254.44（77.55） |
| 20 | 30.53（9.31） | 47.71（14.54） | 74.54（22.72） | 190.83（58.16） |
| 25 | 24.43（7.45） | 38.17（11.63） | 59.63（18.18） | 152.66（46.53） |
| 30 | 20.35（6.20） | 31.80（9.69） | 49.69（15.15） | 127.22（38.78） |
| 35 | 17.45（5.32） | 27.26（8.31） | 42.60（12.98） | 109.04（33.24） |
| 40 | 15.27（4.65） | 23.85（7.27） | 37.27（11.36） | 95.41（29.08） |
| 45 | 13.57（4.14） | 21.20（6.46） | 33.13（10.10） | 84.81（28.85） |
| 50 | 12.21（3.72） | 19.08（5.82） | 29.82（9.09） | 76.33（23.27） |
| 55 | 11.10（3.38） | 17.35（5.29） | 27.11（8.26） | 69.39（21.15） |
| 60 | 10.18（3.10） | 15.90（4.85） | 24.85（7.57） | 63.61（19.39） |
| 65 | 9.39（2.86） | 14.68（4.47） | 22.94（6.99） | 58.72（17.90） |
| 70 | 8.72（2.66） | 13.63（4.15） | 21.30（6.49） | 54.52（16.62） |
| 75 | 8.14（2.48） | 12.72（3.88） | 19.88（6.06） | 50.89（15.51） |
| 80 | 7.63（2.33） | 11.93（3.64） | 18.64（5.68） | 47.71（14.54） |
| 85 | 7.18（2.19） | 11.23（3.42） | 17.54（5.35） | 44.90（13.69） |
| 90 | 6.78（2.07） | 10.60（3.23） | 16.56（5.05） | 42.41（12.93） |
| 95 | 6.43（1.96） | 10.04（3.06） | 15.69（4.78） | 40.17（12.25） |
| 100 | 6.11（1.86） | 9.54（2.91） | 14.91（4.54） | 38.17（11.63） |

# APPENDIX V WIRE GAUGE REFERENCE SHEET

| Metric bare wire diameter （mm） | AWG | SWG | Bare wire cross section （mm2） |
| --- | --- | --- | --- |
| 0.050 | 43 | 47 | 0.00196 |
| 0.060 | 42 | 46 | 0.00283 |
| 0.070 | 41 | 45 | 0.00385 |
| 0.080 | 40 | 44 | 0.00503 |
| 0.090 | 39 | 43 | 0.00636 |
| 0.100 | 38 | 42 | 0.00785 |
| 0.110 | 37 | 41 | 0.00950 |
| 0.130 | 36 | 39 | 0.01327 |
| 0.140 | 35 | / | 0.01539 |
| 0.160 | 34 | 37 | 0.02011 |
| 0.180 | 33 | / | 0.02545 |
| 0.200 | 32 | 35 | 0.03142 |
| 0.230 | 31 | / | 0.04115 |
| 0.250 | 30 | 33 | 0.04909 |
| 0.290 | 29 | 31 | 0.06605 |
| 0.330 | 28 | 30 | 0.08553 |
| 0.350 | 27 | 29 | 0.09621 |
| 0.400 | 26 | 28 | 0.1257 |
| 0.450 | 25 | / | 0.1602 |
| 0.560 | 24 | 24 | 0.2463 |
| 0.600 | 23 | 23 | 0.2827 |
| 0.710 | 22 | 22 | 0.3958 |
| 0.750 | 21 | / | 0.4417 |
| 0.800 | 20 | 21 | 0.5027 |
| 0.900 | 19 | 20 | 0.6362 |
| 1.000 | 18 | 19 | 0.7854 |
| 1.250 | 16 | 18 | 1.2266 |
| 1.500 | 15 | / | 1.7663 |
| 2.000 | 12 | 14 | 3.1420 |
| 2.500 | / | / | 4.9080 |
| 3.000 | / | / | 7.0683 |

Note

- This manual is for reference only. Slight difference may be found in the user interface.

- All the designs and software here are subject to change without prior written notice.

- All trademarks and registered trademarks are the properties of their respective owners.

- If there is any uncertainty or controversy, please refer to the final explanation of us.

- Please visit our website or contact your local service engineer for more information.